## Instructions
Acoustic Performance Calculator LEED v4.1 EQ Prerequisite Minimum Acoustic Performance and EQ Credit Acoustic Performance
Step 1.
Enable macros.
Note: This calculator is for use with Excel for Mac 2011 and Excel 2007 or later.
Step 2.
Unit of measurement | IP units
Note: This selection must match the unit of measurement chosen during project registration.
Step 3.
Complete at least two of the following tabs:
Background Noise
Sound Transmission (Isolation)
Reverberation Time
For Schools projects
For classrooms and core learning spaces less than 20,000 cu ft (566 cu m)
Option 1. Complete the following tabs:
Background Noise
Noise Reduction Coefficient
Option 2. Complete the following tabs:
Background Noise
Reverberation Time
For classrooms and core learning spaces greater than or equal to 20,000 cu ft (566 cu m)
Complete the following tabs:
Background Noise
Reverberation Time
For projects attempting EQ Credit Acoustic Performance, complete the Sound Transmission tab.
For Healthcare projects
Option 1. Complete the following tabs:
Background Noise
Sound Transmission (Isolation)
Speech Privacy
Option 2. Complete the Acoustical Finishes tab.
Step 4.
Upload the completed spreadsheet to LEED Online. Complete any related summary fields in the LEED credit form with the results of the calculator.
UOM
|  | V01 | 1
|  | Copyright © 2019 | IP = 1, SI = 2
U.S. Green Building Council
All Rights Reserved
Last updated 11/12/2019

## Assumptions
Assumptions
Background Noise
Space Type |  | Sound Rating Method
|  | NC/RC | dBA | dBC | RC (N)
2015 ASHRAE Handbook—HVAC Applications (Chapter 48, Table 1) and AHRI 885-2008 (Table 15) | Rooms with intrusion from outdoor noise sources - Traffic noise | n/a | 45 | 70 | n/a
| Rooms with intrusion from outdoor noise sources - Aircraft flyovers | n/a | 45 | 70 | n/a
| Residences, apartments, condominiums - Living areas | 30 | 35 | 60 | 35
| Residences, apartments, condominiums - Bathrooms, kitchens, utility rooms | 35 | 40 | 60 | 35
| Hotels/motels - Individual rooms or suites | 30 | 35 | 60 | 35
| Hotels/motels - Meeting/banquet rooms | 30 | 35 | 60 | 35
| Hotels/motels - Corridors and lobbies | 40 | 45 | 65 | 45
| Hotels/motels - Service/support areas | 40 | 45 | 65 | 45
| Office buildings - Executive and private offices | 30 | 35 | 60 | 35
| Office buildings - Conference rooms | 30 | 35 | 60 | 35
| Office buildings - Teleconference rooms | 25 | 30 | 55 | 25
| Office buildings - Open-plan offices | 40 | 45 | 65 | 40
| Office buildings - Corridors and lobbies | 40 | 45 | 65 | 45
| Courtrooms - Unamplified speech | 30 | 35 | 60 | 35
| Courtrooms - Amplified speech | 35 | 40 | 60 | 40
| Performing arts spaces - Drama theaters, concert and recital halls | 20 | 25 | 50 | 25
| Performing arts spaces - Music teaching studios | 25 | 30 | 55 | 25
| Performing arts spaces - Music practice rooms | 30 | 35 | 60 | 35
| Hospitals and clinics - Patient rooms | 30 | 35 | 60 | 35
| Hospitals and clinics - Wards | 35 | 40 | 60 | 40
| Hospitals and clinics - Operating and procedure rooms | 35 | 40 | 60 | 35
| Hospitals and clinics - Corridors and lobbies | 40 | 45 | 65 | 40
| Laboratories - Testing/research with minimal speech communication | 50 | 55 | 75 | 55
| Laboratories - Extensive phone use and speech communication | 45 | 50 | 70 | 50
| Laboratories - Group teaching | 35 | 40 | 60 | 45
| Churches, mosques, synagogues - General assembly with critical music programs | 25 | 30 | 55 | 35
| Schools - Classrooms | 30 | 35 | 60 | 30
| Schools - Large lecture rooms with speech amplification | 30 | 35 | 60 | 30
| Schools - Large lecture rooms without speech amplification | 25 | 30 | 55 | 25
| Libraries - Libraries | 30 | 35 | 60 | 40
| Indoor Stadiums, gymnasium - Gymnasiums and natatoriums | 45 | 50 | 60 | 50
| Indoor Stadiums, gymnasium - Large-seating-capacity spaces with speech amplification | 50 | 55 | 75 | 55
2018 FGI Guidelines Outpatient, Hospital(Table 1.2-52), Residential (Table 2.5-5) | Patient rooms | 40 | 45 | n/a | 40
| NICU sleep area | 30 | 35 | n/a | 30
| NICU staff and family areas | 35 | 40 | n/a | 35
| Medication safety zone | 40 | 45 | n/a | 40
| Multiple- occupant patient care areas | 45 | 50 | n/a | 45
| Examination / treatment room | 40 | 45 | n/a | 40
| Procedure room | 40 | 45 | n/a | 40
| Class 2 imaging room | 40 | 45 | n/a | 40
| Operating rooms | 50 | 55 | n/a | 50
| Class 3 imaging room | 50 | 55 | n/a | 50
| Testing/research lab, minimal speech | 55 | 60 | n/a | 55
| Research lab, extensive speech | 50 | 55 | n/a | 50
| Group teaching lab | 45 | 50 | n/a | 45
| Corridors and public area | 45 | 50 | n/a | 45
| Conference rooms | 35 | 40 | n/a | 35
| Teleconferencing rooms | 25 | 30 | n/a | 25
| Auditoriums, | 30 | 35 | n/a | 30
| Large lecture rooms | 30 | 35 | n/a | 30
| Private office | 40 | 45 | n/a | 40
| Examination/special purpose examination room | 40 | 45 | n/a | 40
| Office, examination room | 40 | 45 | n/a | 40
| Heathcare- Resident rooms/dwelling units | 40 | 45 | n/a | 40
| Medication room | 35 | 40 | n/a | 35
| Multiple occupant resident care area | 45 | 50 | n/a | 45
| Corridors, community space | 45 | 50 | n/a | 45
| Quiet room | 30 | 35 | n/a | 30
| Community meeting room, auditorium | 30 | 35 | n/a | 30
| Communal dining room | 35 | 40 | n/a | 35
| Natatorium | 45 | 50 | n/a | 45
| Medical or pharmacy waiting area | 40 | 45 | n/a | 40
Sound Transmission (Isolation)
Rating System (Table 1) | occupied space- Space use and desired level of acoustic privacy | Space use and desired level of acoustic privacy for the space adjacent to occupied space | STCc ** | STCc adjusted for sound masking | NIC** | NIC adjusted for sound masking | Unique Space Types
| Collaborative / multi-use | Hallway / stairway | 25 | 20 | 20 | 15
| Collaborative / multi-use | Collaborative / multi-use | 35 | 30 | 30 | 25 | Residence (within a multifamily residence), hotel, or motel room
| Collaborative / multi-use | Private | 45 | 40 | 40 | 35 | Residence, hotel or motel room
| Collaborative / multi-use | Confidential | 50 | 45 | 45 | 40 | Retail
| Collaborative / multi-use | Mechanical equipment room | 60 | n/a | 55 | n/a | Standard office
| Collaborative / multi-use | Other (specify) | specify | specify | specify | specify | Executive office
| Private | Hallway / stairway | 35 | 30 | 30 | 25 | Conference room
| Private | Collaborative / multi-use | 45 | 40 | 40 | 35 | Office, conference room
| Private | Private | 45 | 40 | 40 | 35 | Mechanical equipment room
| Private | Confidential | 50 | 45 | 45 | 40 | Classroom or other core learning space
| Private | Mechanical equipment room | 60 | 55 | 55 | n/a | Patient room
| Private | Other (specify) | specify | specify | specify | specify | NICU room
| Confidential | Hallway / stairway | 40 | 35 | 35 | 30 | NICU
| Confidential | Collaborative/ multi-use | 50 | 45 | 45 | 40 | Exam room
| Confidential | Private | 50 | 45 | 45 | 40 | Treatment room
| Confidential | Confidential | 50 | 45 | 45 | 40 | Toilet room
| Confidential | Mechanical equipment room* | 60 | 55 | 55 | n/a | Consultation room
| Confidential | Other (specify) | specify | specify | specify | specify | Public space
| Conference room | Conference room | 50 | 45 | 45 | 40 | Other
| Conference room | Other (specify) | specify | specify | specify | specify
| Conference room | Retail | 50 | 45 | 45 | 40
| Retail | Other (specify) | specify | specify | specify | specify
| Mechanical equipment room* | Hallway / stairway | 50 | n/a | 45 | n/a
| Mechanical equipment room* | Occupied area | 60 | n/a | 55 | n/a
| Other (specify) | Other (specify) | Specify | Specify | Specify | specify
| Adjacency Combinations |  |  |  | STCc Rating
ANSI S12.60–2010 Part 1 (Table 4) | Classroom or other core learning space | Other enclosed or open-plan core learning space |  |  | 50
| Classroom or other core learning space | Therapy room |  |  | 50
| Classroom or other core learning space | Health care room |  |  | 50
| Classroom or other core learning space | Other space requiring a high degree of acoustical privacy |  |  | 50
| Classroom or other core learning space | Common-use and public-use toilet room |  |  | 53
| Classroom or other core learning space | Common-use and public-use bathing room |  |  | 53
| Classroom or other core learning space | Corridor |  |  | 45
| Classroom or other core learning space | Staircase |  |  | 45
| Classroom or other core learning space | Office |  |  | 45
| Classroom or other core learning space | Conference room |  |  | 45
| Classroom or other core learning space | Music room |  |  | 60
| Classroom or other core learning space | Music performance space |  |  | 60
| Classroom or other core learning space | Auditorium |  |  | 60
| Classroom or other core learning space | Mechanical equipment room |  |  | 60
| Classroom or other core learning space | Cafeteria |  |  | 60
| Classroom or other core learning space | Gymnasium |  |  | 60
| Classroom or other core learning space | Indoor swimming pool |  |  | 60
| Classroom or other core learning space | Other (Specify) |  |  | (specify)
2018 FGI Guidelines Outpatient, Hospital (Table 1.2-6) , Residential (Table 2.5-5) | Patient room | Patient room (wall - same floor) |  |  | 45
| Patient room | Patient room (floor-to-floor) |  |  | 50
| Patient room | Corridor (with entrance) |  |  | 35
| Patient room | Public space |  |  | 50
| Patient room | Service area |  |  | 60
| Patient room | MRI room |  |  | 60
| Patient room | Other (Specify) |  |  | (specify)
| Examination room | Corridor (with entrance) |  |  | 35
| Examination room | Public space |  |  | 50
| Examination room | MRI room |  |  | 60
| Examination room | Examination room (no electronic masking) |  |  | 50
| Examination room | Examination room (with electronic masking) |  |  | 40
| Examination room | Other (Specify) |  |  | (specify)
| Examination room | Multiple-occupant resident care and activity areas or public corridor |  |  | 50
| Treatment room | Treatment room |  |  | 50
| Treatment room | Corridor (with entrance) |  |  | 35
| Treatment room | Other (Specify) |  |  | (specify)
| Operating room | Operating room |  |  | 50
| Operating room | MRI scanner room |  |  | 60
| Operating room | Other (Specify) |  |  | (specify)
| Toilet room | Public space |  |  | 45
| Toilet room | Multiple-occupant resident care and activity areas or public corridor |  |  | 45
| Toilet room | Other (Specify) |  |  | (specify)
| Consultation room | Public space |  |  | 50
| Consultation room | Corridor (with entrance) |  |  | 35
| Consultation room | Other (Specify) |  |  | (specify)
| Public space | MRI scanner room |  |  | 50
| Resident room/dwelling unit | Resident room/dwelling unit |  |  | 45
| Resident room/dwelling unit | Corridor (with entrance) |  |  | 35
| Resident room/dwelling unit | Community space |  |  | 50
| Resident room/dwelling unit | Service area |  |  | 60
| Care consultation room | Multiple-occupant resident care and activity areas or public corridor |  |  | 50
| Care consultation room | Resident room/dwelling unit |  |  | 50
| Care consultation room | Corridor (with entrance) |  |  | 35
| Other | (specify) |  |  | (specify)
Reverberation Time
| Room and Application Type | T60 (sec)
| Hotel/motel - individual room or suite | 0.6
| Hotel/motel - meeting or banquet room | 0.8
| Office building - executive or private office | 0.6
| Office building - conference room | 0.6
| Office building - teleconference room | 0.6
| Office building - open-plan office without sound masking | 0.8
| Office building - open-plan office with sound masking | 0.8
| Courtroom - unamplified speech | 0.7
| Courtroom - amplified speech | 1
| Performing arts space - drama theaters, concert and recital halls | (specify)
| Laboratories - testing or research with minimal speech communication | 1
| Laboratories - extensive phone use and speech communication | 0.6
| Church, mosque, synagogue - general assembly with critical music program | (specify)
| Library | 1
| Indoor stadium, gymnasium - gymnasium and natatorium | 2
| Indoor stadium, gymnasium - large-capacity space with speech amplification | 1.5
| Other | (specify)
| For Schools: Classroom and other core learning space | (specify)
Speech Privacy
| Enclosed or Open | Speech Privacy Goal |  | Design Criteria | Threshold |  | Enclosed | Open
2010 FGI Guidelines (Table 1.2-4) | Enclosed | Normal |  | PI | > | 85 | Normal | Normal (non-intrusive)
| Enclosed | Normal |  | AI | < | 0.15 | Confidential | Confidential
| Enclosed | Normal |  | STI | < | 0.19 | Secure
| Enclosed | Normal |  | SII | < | 0.2
| Enclosed | Confidential |  | PI | > | 95
| Enclosed | Confidential |  | AI | < | 0.05
| Enclosed | Confidential |  | STI | < | 0.12
| Enclosed | Confidential |  | SII | < | 0.1
| Enclosed | Secure |  | n/a |  | 0
| Open | Normal (non-intrusive) |  | PI | > | 80
| Open | Normal (non-intrusive) |  | AI | < | 0.2
| Open | Normal (non-intrusive) |  | STI | < | 0.23
| Open | Normal (non-intrusive) |  | SII | < | 0.25
| Open | Confidential |  | n/a |  | 0
Acoustical Finishes
| Space Type | Design Coefficient
2018 FGI Guidelines Hospitals, Outpatient (Table 1.2-4), Residential (Table 2.5-5) | Private patient room | 0.15
| Multi-bed patient room | 0.15
| Corridor (near patient area) | 0.15
| Medication safety zone | 0.15
| Nurse station | 0.15
| Waiting area (near patient area) | 0.25
| Atrium | 0.1
| Office | 0.15
| Examination room | 0.15
| Treatment room | 0.15
| Procedure room | 0.15
| Class 2 imaging room | 0.15
| Operating room | n/a
| Class 3 imaging room | n/a
| Corridor (public corridor in residential care areas) | 0.2
| Medication rooms | 0.2
| Multiple occupant resident care and activity areas | 0.2
| Quiet room | 0.2
| Natatorium | 0.1
| Dining room with more than 50 occupants | n/a

## Background Noise
Background Noise
For New Construction, Data Centers, Warehouses and Distribution Centers, and Hospitality projects: Complete the table to demonstrate that the background noise requirements will be met in all occupied spaces. Include background noise from all HVAC systems. Include all acoustically critical spaces/room types or worst case combinations of room assemblies and noise sources. For Schools projects: Complete the table to demonstrate that the background noise requirements will be met in all classrooms and other core learning spaces. Include background noise from all HVAC systems. Include all acoustically critical spaces/room types or worst case combinations of room assemblies and noise sources. For Healthcare projects: Complete the table to demonstrate that the background noise requirements will be met in all occupied spaces. Include background noise from all building mechanical-electrical-plumbing systems, air distribution systems and other noise sources under the purview of the project team. Include all acoustically critical spaces/room types or worst case combinations of room assemblies and noise sources.
| Space ID | Space Type | For all except Schools projects |  |  |  | For Schools projects
|  |  | Sound Rating Method | Maximum Allowed Background Noise Level | Background Noise Level | Background Noise Compliance | Prerequisite Maximum Allowed Background Noise Level (dBA) | Credit Maximum Allowed Background Noise Level (dBA) | Background Noise Level (dBA) | Background Noise Level Prerequisite Compliance | Background Noise Level Credit Compliance
0 |  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
0 |  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
0 |  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
0 |  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
0 |  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
0 |  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
0 |  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
0 |  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
|  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
|  |  |  | 0 |  | N/A | 40 | 35 |  | N/A | N/A
A | For all except Schools projects | The background noise levels in all spaces do not exceed the maximum background noise level |  |  |  | N/A
| For Schools projects | Prerequisite: The background noise levels in all spaces do not exceed 40 dBA | [8 empty] | N/A
|  | Credit: The background noise levels in all spaces do not exceed 35 dBA | [8 empty] | N/A
Add Rows
Delete Rows
Note on F7: The maximum allowed background noise levels are listed in 2015 ASHRAE Handbook, Chapter 48, Table 1 (page 48.3) or AHRI Standard 885-2008, Table 15 (page 33). For Healthcare, the maximum allowed background noise levels are listed in Table 1.2-5 of the 2018 FGI Guidelines for Design and Construction of Hospitals, Table 1.2-5 of the 2018 FGI Guidelines for Design and Construction of Outpatient Facilities, Table 2.5-5 of the 2018 FGI Guidelines for Design and Construction of Residential Health, or 2015 ASHRAE Handbook, Chapter 48, Table 1 (page 48.3).

## Sound Transmission
Sound Transmission
Complete the table to demonstrate that the sound transmission class or noise isolation class requirements will be met in all occupied spaces. Include all acoustically critical spaces/room types or worst case combinations of room assemblies.
| Room ID | Space Description | Space use and desired level of acoustic privacy | Space use and desired level of acoustic privacy for the adjacent space | Is sound masking being used and compliant with the credit requirements? | STC or NIC for compliance? | Minimum Required [STCc rating OR NIC value] | STCc rating OR NIC value | Sound Transmission Compliance
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
[7 empty] | 0 |  | N/A
[7 empty] | 0 |  | N/A
A | The sound transmission requirements are met for each space | [7 empty] | N/A
Add Rows
Delete Rows
Note on B6: Rooms may be grouped into a single room type if their floor assemblies, ceiling assemblies, wall assemblies and adjacent spaces are identical.
Note on I6: The STC rating should account for all materials and layers in the assembly. This calculator does not compute composite STC.

## Sound Transmission (SCH, HC)
Sound Transmission (Isolation)
For Healthcare projects: Complete the table to demonstrate that the sound isolation requirements will be met in all occupied spaces. Include all acoustically critical spaces/room types or worst case combinations of room assemblies. For Schools projects: Complete the table to demonstrate that the sound transmission requirements will be met in all classrooms and other core learning spaces. Include all acoustically critical spaces/room types or worst case combinations of room assemblies. It is not acceptable to list a single STC value for the room, each surface (plane surrounding the space) should have a separate assembly, so at least one floor/ceiling & one wall assembly must be entered.
| Room ID | Assembly ID | Assembly Description | Assembly Location | Space Type | Adjacent Space Type | Minimum Required STCc Rating | STCc Rating | Sound Transmission Compliance
0 |  |  |  |  | Examination room |  | 0 |  | No
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
0 | [6 empty] | 0 |  | N/A
[7 empty] | 0 |  | N/A
[7 empty] | 0 |  | N/A
A | The sound transmission requirements are met for each space | [7 empty] | No
Add Rows
Delete Rows
Note on B6: Rooms may be grouped into a single room type if their floor assemblies, ceiling assemblies, wall assemblies and adjacent spaces are identical.
Note on I6: The STC rating should account for all materials and layers in the assembly. This calculator does not compute composite STC.

## Reverberation Time
Reverberation Time
Complete the table with calculations or measurements for all acoustically critical spaces/room types or worst case combinations of room assemblies. Rooms may be grouped into a single room type if their floor assemblies, ceiling assemblies, wall assemblies and adjacent spaces are identical. For each space, all surface materials and their associated surface area must be listed.
[7 empty] | 0 |  |  |  |  | 0
| Material ID | Description of Material | Manufacturer or Vendor Name | Sound Absorption Coefficient |  |  | Space ID |  |  |  |  | Space ID
[7 empty] | Space and Application Type |  |  |  |  | Space and Application Type
|  |  |  | 500 Hz | 1000 Hz | 2000 Hz | Surface Area (sq ft) | Material Location | Equivalent Sound Absorption at 500 Hz | Equivalent Sound Absorption at 1000 Hz | Equivalent Sound Absorption at 2000 Hz | Surface Area (sq ft) | Material Location | Equivalent Sound Absorption at 500 Hz | Equivalent Sound Absorption at 1000 Hz | Equivalent Sound Absorption at 2000 Hz
0 | [8 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
0 | [8 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
0 | [8 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
0 | [8 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
0 | [8 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
0 | [8 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
0 | [8 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
0 | [8 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
[9 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
A | Room volume (cubic feet)
| Total sound absorbing units (sabins) | [7 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
| Reverberation time requirement (s) | [7 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
| Reverberation time (s) | [7 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0
| The reverberation time was not exceeded | [5 empty] | 0 |  |  |  | N/A | 0 |  |  |  | N/A
Note on B22: The reverberation time requirements are listed in Table 2 of the rating system language. For Schools projects, identify the reverberation time requirements from ANSI Standard S12.60-2010 or NRC-CNRC Construction Technology Update No. 51, Acoustical Design of Rooms for Speech (2002), depending on classroom and other core learning space size.
Add Rows
Add Space
Delete Rows
Delete Space

## Noise Reduction Coefficient
Noise Reduction Coefficient
For Schools projects only
Complete the table. Rooms may be grouped into a single core learning space/model if their construction is identical. Only the materials that demonstrate compliance with the requirements must be listed.
[5 empty] | 0 |  | 0 |  | 0
| Material ID | Description of Material | Manufacturer or Vendor Name | NRC | Space ID |  | Space ID |  | Space ID
[5 empty] | Area of Material (sq ft) | NRC Compliance | Area of Material (sq ft) | NRC Compliance | Area of Material (sq ft) | NRC Compliance
0 | [5 empty] | N/A |  | N/A |  | N/A
0 | [5 empty] | N/A |  | N/A |  | N/A
0 | [5 empty] | N/A |  | N/A |  | N/A
0 | [5 empty] | N/A |  | N/A |  | N/A
0 | [5 empty] | N/A |  | N/A |  | N/A
0 | [5 empty] | N/A |  | N/A |  | N/A
0 | [5 empty] | N/A |  | N/A |  | N/A
0 | [5 empty] | N/A |  | N/A |  | N/A
[6 empty] | N/A |  | N/A |  | N/A
[6 empty] | N/A |  | N/A |  | N/A
A | Total ceiling area, excluding lights, diffusers, and grilles (sq ft)
| Area of qualifying material with NRC of 0.70 or higher (sq ft) |  |  |  |  | 0 |  | 0 |  | 0
| The sound absorptive materials requirement is met for each space |  |  |  |  | N/A |  | N/A |  | N/A
Add Rows
Add Space
Delete Rows
Delete Space

## Speech Privacy
Speech Privacy
For Healthcare projects only
Complete the table with either calculations or measurements for all acoustically critical spaces/room types or worst case combinations of room assemblies and noise sources.
| Space Name or ID | Space Type | Enclosed or Open-plan | Speech Privacy Goal | Design Criteria | Minimum or Maximum Accepted Value | Speech Privacy Value | Speech Privacy Compliance
0 | [7 empty] | N/A
0 | [7 empty] | N/A
0 | [7 empty] | N/A
0 | [7 empty] | N/A
0 | [7 empty] | N/A
0 | [7 empty] | N/A
0 | [7 empty] | N/A
0 | [7 empty] | N/A
N/A
N/A
A | Speech privacy criteria has been met for all spaces | [6 empty] | N/A
Add Rows
Delete Rows

## Acoustical Finishes
Acoustical Finishes
For Healthcare projects only
Complete the table for all acoustically critical spaces/room types or worst case combinations of room assemblies. Rooms may be grouped into a single room type if their floor assemblies, ceiling assemblies, and wall assemblies are identical.
[5 empty] | 0 |  | 0 |  | 0
| Material or Surface ID | Description of Material or Surface | Manufacturer or Vendor Name (for materials only) | NRC (α) | Room ID |  | Room ID |  | Room ID
[5 empty] | Room Type |  | Room Type |  | Room Type
[5 empty] | Surface Area (sq ft) | Sα | Surface Area (sq ft) | Sα | Surface Area (sq ft) | Sα
0
0
0
0
0
0
0
0
A | Total room surface area (sq ft)
Recommended design room sound absorption coefficient (αdesign)
Average sound absorption coefficient (αaverage)
Acoustical finishes criteria have been met for each space
Add Rows
Add Space
Delete Rows
Delete Space

## Summary D+C
Summary
Note: All information on this tab is READ-ONLY. To edit, see the previous tabs.
Background Noise
The background noise levels in all spaces do not exceed the maximum background noise level | N/A
Sound Transmission
The sound transmission requirements are met for each space | N/A
Reverberation Time
The reverberation time for each space was not exceeded | N/A

## Summary SCH
Summary for Schools
Note: All information on this tab is READ-ONLY. To edit, see the previous tabs.
EQ Prerequisite Minimum Acoustic Performance
HVAC Background Noise
The background noise levels in all spaces do not exceed 40 dBA | N/A
Reverberation Time
For classrooms and core learning spaces less than 20,000 cu ft (566 cu m)
Option 1. The sound absorptive materials requirement is met for each space (Noise Reduction Coefficient tab) | N/A
Option 2. The reverberation time for each space was not exceeded (Reverberation Time tab) | N/A
For classrooms and core learning spaces greater than or equal to 20,000 cu ft (566 cu m)
The reverberation time for each space was not exceeded (Reverberation Time tab) | N/A
EQ Credit Acoustic Performance
HVAC Background Noise
The background noise levels in all spaces do not exceed 35 dBA | N/A
Sound Transmission
The sound transmission requirements are met for each space | No

## Summary HC
Summary for Healthcare
Note: All information on this tab is READ-ONLY. To edit, see the previous tabs.
Option 1. Speech Privacy, Sound Isolation, and Background Noise
Speech Privacy
Speech privacy criteria has been met for each space | N/A
Sound Isolation
The sound transmission requirements are met for each space | No
Background Noise
The background noise levels in all spaces do not exceed the maximum background noise level | N/A
Option 2. Acoustical Finishes and Site Exterior Noise
Acoustical Finishes
Acoustical finishes criteria have been met for each space | N/A